## Slide 1
MINI PROJECT REPORT
Single Phase
Power Monitor
Real-Time Voltage, Current & Power Measurement
Maharudra Patil | Parth Kulkarni | Sarvesh Malani
Dept. of Electronics Engineering, Walchand Institute of Technology, Solapur | 2025-26

## Slide 2
Problem Statement & Objectives
⚡ The Problem
Traditional meters show only cumulative usage — no real-time insight.
Voltage fluctuations damage sensitive equipment.
Undetected current surges cause overloading hazards.
Affordable real-time monitoring tools are unavailable for small users.
Increased electricity bills from unmonitored consumption.
🎯 Objectives
Measure RMS voltage and current in real time.
Calculate instantaneous active power (P = V × I).
Track cumulative energy consumption (Wh).
Display parameters live on OLED display.
Build a low-cost (<₹700), portable, compact solution.

## Slide 3
System Block Diagram
AC Supply
230V / 50Hz
ZMPT101B
Voltage Sensor
ACS712
Current Sensor
Arduino Nano
(ATmega328P)
ADC + Processing
OLED Display
(SSD1306)
0.96" I2C
A0
A1
I2C
Signal flow: AC mains → Sensors (analog out) → Arduino ADC (A0/A1) → Computation → OLED via I²C bus

## Slide 4
Key Components
⚡
ZMPT101B
Voltage Sensor
Measures AC up to 250V
Galvanic isolation
0–5V output, 2.5V offset
🔌
ACS712
Current Sensor
Hall-effect, 5A range
185 mV/A sensitivity
Galvanic isolation
🖥
Arduino Nano
Microcontroller
ATmega328P @ 16 MHz
10-bit ADC, 6 analog pins
32 KB Flash memory
📺
OLED SSD1306
Display
0.96", 128×64 pixels
I2C protocol (A4/A5)
High contrast, 3.3–5V

## Slide 5
Working Principle
01
Signal Sensing
ZMPT101B & ACS712 simultaneously sense AC voltage and current, producing safe 0–5V analog signals centred at 2.5V.
02
ADC Sampling
Arduino Nano samples 1000 data points from A0 & A1 within one complete 20ms AC cycle (50Hz).
03
RMS Calculation
Instantaneous values are squared, averaged over the full cycle, and square-rooted:
V_rms = √(Σv²/N), I_rms = √(Σi²/N)
04
Power & Energy
Active Power: P = V_rms × I_rms (PF = 1 for resistive loads).
Energy is accumulated by integrating P over time (Wh).
05
Display Update
All four values (V, A, W, Wh) are rendered on the OLED every 1 second using a millis()-based non-blocking timer.

## Slide 6
Hardware Design & Circuit
Pin Connections
Module
Pin
Arduino
ZMPT101B
OUT
A0
ACS712
OUT
A1
OLED SSD1306
SDA
A4
OLED SSD1306
SCL
A5
ZMPT101B/ACS712
VCC
5V
OLED SSD1306
VCC
3.3V
All Modules
GND
GND
Design Considerations
🔒
Safety & Isolation
ZMPT101B & ACS712 provide galvanic isolation from mains — microcontroller is fully protected.
📐
ADC Reference
Both sensors biased at 2.5V offset, fitting the 0–5V ADC range without signal clipping.
🔇
Noise Filtering
100µF cap on ZMPT101B output and 10nF on ACS712 FILTER pin reduce switching noise.
💰
Cost Efficiency
All components are off-the-shelf. Total BOM cost: ₹500–₹700 only.

## Slide 7
Software Design & Implementation
🛠 Tools Used
Arduino IDE v2.x — compile & upload firmware
Embedded C / Arduino C++ — programming language
Adafruit SSD1306 & GFX Library — OLED driver
Proteus 8 Professional — circuit simulation
Serial Monitor — debugging & calibration
📄 Core Firmware Logic
double sumV = 0, sumI = 0;
for (int i = 0; i < 1000; i++) {
double v = (analogRead(A0)*5.0/1023.0 - 2.5)
* vCal;
double c = (analogRead(A1)*5.0/1023.0 - 2.5)
/ 0.185;
sumV += v * v;
sumI += c * c;
}
float Vrms = sqrt(sumV / 1000);
float Irms = sqrt(sumI / 1000);
float Power = Vrms * Irms;
// Display refreshed every 1 s via millis()

## Slide 8
Testing & Results
Parameter
Measured Value
Actual Value
Error (%)
Voltage
219.4 V
220 V
0.27%
Current
1.98 A
2.0 A
1.0%
Power (Calculated)
434.0 W
440 W
1.36%
Frequency
49.8 Hz
50 Hz
0.40%
Load: 100W incandescent lamp @ 230V AC mains | Reference: Calibrated DMM + Clamp meter
0.27%
Voltage Accuracy Error
1.0%
Current Accuracy Error
1.36%
Power Accuracy Error
0.40%
Frequency Error

## Slide 9
Achievements & Future Scope
✅ Achievements
Real-time V, I, P, Energy on compact OLED display.
Voltage accuracy: 0.27% | Power accuracy: 1.36%.
Calibrated & debugged ACS712 offset and ADC noise.
Validated via Proteus simulation before hardware.
Total cost under ₹700 — affordable & portable.
🚀 Future Scope
IoT Integration — ESP8266/ESP32 for remote web dashboard.
True Power Factor — measure reactive & apparent power.
Data Logging — SD card / EEPROM for historical analysis.
Multi-Phase Extension — 3-phase industrial systems.
Cloud Integration — ThingSpeak / Blynk for alerts.
Thank You | Department of Electronics Engineering, Walchand Institute of Technology, Solapur | 2025-26

## Slide 10
Conclusion
The Single Phase Power Monitor project successfully demonstrates a low-cost and efficient system for real-time measurement of electrical parameters such as voltage, current, power, and energy. Using Arduino and sensors, the system provides accurate readings and helps users monitor electricity usage effectively. This project is useful for reducing energy wastage and improving power management. Overall, it is a simple, compact, and practical solution that can be further enhanced with advanced features like IoT-based remote monitoring.